## README
BESS hazardous scenarios – source workbook for the HTML page
This workbook is the single source for the HTML. Edit it, then upload it and ask Claude to rebuild the HTML (or run build_html.py yourself: python build_html.py this_file.xlsx).
Rules
• Do not rename sheets or header cells (row 1). Add rows at the bottom of a table; delete a row to remove an item. Column order may not change.
• Cells with several items: put ONE ITEM PER LINE inside the cell (Alt+Enter in Excel). Used in: Sequence steps, Consequences, Hazards, Hazard types.
• SF IDs in Scenarios: comma-separated, e.g. SF-01, SF-11. The 'Covers' list of each safety function is built automatically from this column – do not maintain it twice.
• Component, Group, Primary hazard type and Hazard types must match a name in the Lists sheet (dropdowns help). A new component needs a row in Lists with a colour.
• Final element tags (Safety functions): semicolon-separated short names. They drive the 'Shared elements' bars. Use the same spelling for the same device.
• Page text: plain text. Write a scenario ID in square brackets, e.g. [OC-03], to turn it into a clickable link.
• Grey columns are formulas (checks only). They are ignored by the HTML builder.
Sheets
Scenarios – one row per initiating event (IE = technical condition + mechanism → sequence → consequences → hazard).
Safety functions – one row per SF: sensor → logic solver → final element.
Other measures – passive / design / administrative measures (no sensor–logic–actuator).
Lists – components (colour, PCS/BMS panel text), groups (order), hazard types (icon, filter), SF types (filter chips).
Page text – headings and notes shown on the page.
Checks – counts and reference checks.

## Scenarios
ID | Group | Component (IE owner) | Operating mode / phase | Initiating event (summary) | IE – Technical condition | IE – Mechanism | Sequence steps (one per line) | Consequences (one per line) | Hazards – person harmed (one per line) | Exposed persons | Primary hazard type | Hazard types (one per line) | Early signal / detectable deviation | SF IDs (comma-separated) | Check: unknown SF IDs
OV-01 | Overcharge / Overvoltage | PCS | Normal operation (charging) | PCS fails to follow BMS charge limit / stop request | PCS charge controller (current/voltage loop) failed – BMS limits and stop request are correct | PCS control or firmware fault ignores the BMS charge limit / stop request and keeps charging (setpoint stuck) | BMS requests stop PCS keeps charging cell overvoltage Li plating / cathode decomposition cell self-heating TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Cell V > Vmax; SOC > 100 %; charge current still flowing at EoC; cell temp rise; off-gas | SF-01, SF-11 | OK
OV-02 | Overcharge / Overvoltage | BMS–PCS comm link | Normal operation (charging) | Loss of BMS–PCS communication with PCS continuing last charge setpoint | Loss of BMS–PCS communication (CAN/Modbus/Ethernet link down) | Link down; PCS has no comm-loss watchdog and keeps running at last received charge setpoint | No charge-limit updates reach PCS charging continues past limits cell overvoltage TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Comm heartbeat lost; cell V rising; SOC > limit | SF-01, SF-02, SF-11 | OK
OV-03 | Overcharge / Overvoltage | BMS | Normal operation (charging) | BMS cell-voltage sensing error causes undetected overcharge | BMS cell-voltage measurement drifts low (AFE / ADC reference drift, wiring resistance) | BMS believes cells are below limit and permits charging while actual cell voltage exceeds Vmax | Measured V < actual V BMS does not request stop real cell overvoltage TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Discrepancy between cell-sum and string voltage; redundant measurement mismatch | SF-01, SF-11 | OK
OV-04 | Overcharge / Overvoltage | BMS | Normal operation (charging) | Single-cell overcharge due to imbalance / balancing failure | Cell imbalance: weak/low-capacity cell or failed balancing circuit | String-level voltage looks normal while one cell is driven above Vmax | Weak cell reaches full charge first continues to be charged with string local overvoltage TR of that cell propagation | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Max-min cell voltage spread increasing; single cell V > Vmax | SF-01, SF-11 | OK
OV-05 | Overcharge / Overvoltage | BMS | Normal operation (charging) | SOC estimation error leads to charging beyond true capacity | SOC estimation error (coulomb-counting drift, wrong OCV table, SOH not updated) | EMS dispatches charge based on false SOC; cells charged beyond true 100 % SOC | EMS charge command continues actual SOC > 100 % overvoltage TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Cell V vs SOC mismatch; V at top limit while SOC < 100 % | SF-01, SF-11 | OK
OV-06 | Overcharge / Overvoltage | BMS | Normal operation (charging) | BMS sends wrong charge limit / no stop request | BMS charge-limit logic failed (software/logic error) – PCS itself works correctly | BMS sends wrong charge limits (CCL/CVL too high) or never sends the end-of-charge request; PCS follows the wrong command | PCS follows BMS command charging continues past limit cell overvoltage TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Cell V > Vmax while BMS CCL > 0; CVL above cell rating | SF-01, SF-11 | OK
OD-01 | Overdischarge / Low-temperature charging | BMS | Idle / long standby, then recharge | Overdischarge followed by recharge of damaged cells | Cells driven below minimum voltage (UV cutoff failed, or parasitic BMS/aux load during long idle) | Copper current collector dissolves; on subsequent recharge Cu redeposits as dendrites | Cell V < Vmin Cu dissolution recharge Cu dendrites pierce separator internal short TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Cell V < Vmin (history); abnormal self-discharge | SF-04 | OK
OD-02 | Overdischarge / Low-temperature charging | Thermal management (HVAC) | Normal operation (charging) in cold climate | Charging at low cell temperature | Enclosure/battery heater failed in cold climate (HVAC heating function) | Cells stay below charge-temperature limit and are charged anyway → lithium plating on anode | Li plating dendrite growth internal short (possibly delayed) TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Cell T < Tmin_charge while I_charge > 0 | SF-05 | OK
OC-01 | Overcurrent / Short circuit | PCS | Normal operation | PCS overcurrent due to current-control failure | PCS current control failure (sensor fault, control loop instability) | Charge/discharge current above cell/busbar rating | Excess current Joule heating in cells, busbars, cables cell overtemperature / insulation melting TR or cable fire | Cell overheating / TR busbar or DC cable overheating and insulation fire arc | Personnel near container/PCS exposed to fire and radiant heat → burns. Personnel inhale toxic smoke from cable/cell fire. | O&M technicians, firefighters | Fire | Fire Toxic | Rack current > Imax; busbar/cable temperature | SF-06 | OK
OC-02 | Overcurrent / Short circuit | DC electrical | Normal operation / maintenance | External DC short circuit | Insulation breakdown between DC+ and DC– (damaged cable, degraded busbar insulation, conductive debris, dropped tool) | Bolted/arcing external short circuit fed by battery (tens of kA) | Very high fault current DC arc, busbar melting, cell heating fire; possible TR | DC arc flash molten metal ejection rack fire possible TR loss of DC isolation | Technician near the rack/combiner is exposed to DC arc flash (thermal burns, eye injury, blast). Personnel exposed to subsequent fire. | O&M technicians | Arc flash | Arc flash Fire | DC fault current; rapid voltage collapse; arc fault detection | SF-06, SF-07 | OK
OC-03 | Overcurrent / Short circuit | DC electrical | Start-up / energization | Pre-charge failure causes contactor welding | Pre-charge circuit failed (resistor open, pre-charge bypassed) | Main contactor closes onto discharged PCS DC-link capacitors → large inrush → contacts weld | Inrush current contactor contacts weld contactor shows 'open' command but stays closed DC side remains energized / isolation lost | Welded contactor (loss of isolation / loss of trip function) DC-link capacitor damage arc | Technician trusts the 'isolated' status and works on DC side that is still live → electric shock / arc flash. | O&M technicians | Electric shock | Electric shock Arc flash | Contactor auxiliary contact vs voltage mismatch; inrush current | SF-08, SF-19 | OK
OC-04 | Overcurrent / Short circuit | DC electrical | Normal operation | Loose / high-resistance electrical connection | High-resistance joint (bolt torque loss from thermal cycling/vibration, corrosion) | Local Joule heating at the joint → hotspot | Hotspot insulation melting / arcing adjacent cell heating TR or rack fire | Local fire at joint arc cell TR of nearby cells | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Arc flash Toxic | Joint temperature; voltage drop across connection; IR thermography | SF-07, SF-09 | OK
IC-01 | Internal cell defect | Battery cell | Normal operation (any SOC) | Internal short circuit from manufacturing defect | Latent manufacturing defect (metal particle, separator defect, electrode misalignment) | Defect grows into internal short circuit during cycling | Internal short local heating TR (can occur even with all controls working) propagation | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Abnormal self-discharge; local temp rise; early off-gas (H2 / VOC) | SF-11, SF-16 | OK
IC-02 | Internal cell defect | Battery cell | Late life | End-of-life degradation leads to internal short | Cell aged beyond SOH limit (SEI growth, gas generation, swelling) | Mechanical stress / separator degradation → internal short | Swelling / separator breach internal short TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | SOH trend; internal resistance rise; swelling | SF-11 | OK
TM-01 | Thermal management / Overtemperature | Thermal management (HVAC) | Normal operation (high C-rate) | Loss of battery cooling during operation | Cooling system failure (compressor trip, fan failure, pump failure / loss of coolant flow) | Heat generated by operation is not removed; cell temperature rises beyond limit | Cell T rises accelerated side reactions self-heating TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Cell / air / coolant temperature; HVAC status; coolant flow | SF-10, SF-16 | OK
TM-02 | Thermal management / Overtemperature | Thermal management (HVAC) | Normal operation (hot season) | Ambient heat exceeds cooling capacity | Extreme ambient heat with undersized or fouled HVAC (blocked condenser, dust, vegetation), solar gain | Cooling capacity insufficient; enclosure and cell temperature exceed limits | Enclosure T rises cell T > limit TR (or accelerated degradation) | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Ambient / enclosure temperature; HVAC load | SF-10 | OK
TM-03 | Thermal management / Overtemperature | BMS | Normal operation | Undetected cell overtemperature due to sensing failure | Cell temperature sensor failure (NTC open/drift reads low) or insufficient sensor coverage | Overtemperature not detected → no derating or trip | Hot cell not seen by BMS continued operation TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Sensor plausibility (neighbour comparison); off-gas | SF-10, SF-11 | OK
TM-04 | Thermal management / Overtemperature | Thermal management (HVAC) | Normal operation | Coolant leak onto energized battery parts | Coolant (water-glycol) leak from hose/fitting/cold plate | Conductive liquid on modules/busbars → tracking, short circuit, ground fault | Leak insulation loss / short arc fire or TR; also loss of cooling | Arc module fire TR ground fault loss of cooling | Personnel exposed to fire/arc → burns. Technician touching wet, energized parts → electric shock. | O&M technicians, firefighters | Fire | Fire Arc flash Electric shock | Leak detection; coolant pressure/level drop; insulation resistance drop | SF-13, SF-17 | OK
ME-01 | Mechanical / External damage | External / site | Any | Vehicle impact on BESS enclosure | Vehicle or forklift impact on enclosure | Enclosure and rack deformation → cell crush/penetration | Cell crush internal short (immediate or delayed) TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS possible crush injury | Driver/personnel at impact point exposed to immediate fire. Personnel near damaged unit later exposed to delayed TR fire/explosion/toxic gas. | Drivers, O&M technicians, firefighters | Fire | Fire Explosion Toxic Mechanical | Impact / shock sensor; sudden cell V drop | SF-14, SF-16 | OK
ME-02 | Mechanical / External damage | External / site | Any | Earthquake causes rack collapse | Seismic event (earthquake) exceeding rack/anchor design | Rack toppling / module drop, cable pull-out | Module/cell damage + cable short arc fire / TR | Rack collapse short circuit arc fire TR | Person inside walk-in enclosure crushed by falling rack/modules. Personnel exposed to fire/arc/toxic gas afterward. | O&M technicians, firefighters | Mechanical | Mechanical Fire Arc flash Toxic | Seismic sensor; multiple rack faults | SF-14 | OK
ME-03 | Mechanical / External damage | People & lifecycle | Installation / module replacement | Module dropped during handling | Lifting equipment or handling failure | Heavy module drops | Drop crush injury; internal cell damage delayed TR | Crush injury damaged cells delayed TR | Worker under/near load crushed. Personnel later exposed to fire from damaged module. | Installers, O&M technicians | Mechanical | Mechanical Fire | — |  | none
EX-01 | External fire / Environment | External / site | Any | External fire exposure | External fire (wildfire, vegetation, adjacent container, transformer fire) | Radiant/convective heat into enclosure → cell heating | External heat cell T rise TR fire spread into and between units | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind, neighbours | Fire | Fire Explosion Toxic | Enclosure external/internal temperature; flame detection | SF-16 | OK
EX-02 | External fire / Environment | External / site | Storm / flooding | Flooding of BESS enclosure | Flood or storm-water ingress (drainage failure, low-lying site) | Modules/busbars submerged; short circuit; electrolysis | Water ingress shorts arc/fire; electrolysis H2 generation (esp. saline water) explosive atmosphere | Short circuit fire H2 accumulation / explosion energized water | Person wading near flooded, energized equipment → electric shock. Personnel exposed to fire/H2 explosion. | O&M technicians, firefighters, public | Electric shock | Electric shock Fire Explosion | Water level sensor; insulation resistance drop | SF-12, SF-15, SF-17 | OK
EX-03 | External fire / Environment | External / site | Thunderstorm | Lightning / surge overvoltage | Lightning strike or switching surge | Overvoltage on DC/AC → insulation breakdown; ground potential rise | Insulation breakdown arc fire; high step/touch voltage around earthing | Equipment insulation failure arc fire ground potential rise | Person on site during strike exposed to step/touch voltage → shock. Personnel exposed to resulting fire. | O&M technicians, public at fence | Electric shock | Electric shock Fire | Surge counter; insulation monitoring |  | none
EX-04 | External fire / Environment | External / site | Normal operation | Condensation inside enclosure | Condensation / high humidity (dehumidification failure, cold surfaces) | Moisture on PCBs/busbars → tracking, BMS malfunction | Tracking arc fire; BMS measurement faults loss of protection | Arc fire BMS malfunction ground fault | Personnel exposed to fire/arc → burns; toxic smoke. | O&M technicians | Fire | Fire Arc flash | Humidity; dew point; insulation resistance | SF-17 | OK
EX-05 | External fire / Environment | External / site | Normal operation | Animal or debris ingress causes insulation damage | Rodent / insect / dust ingress | Insulation chewed or conductive bridging | Insulation damage short arc fire | Arc fire ground fault | Personnel exposed to fire/arc → burns. | O&M technicians | Fire | Fire Arc flash | Insulation resistance; ground-fault alarm | SF-17 | OK
GX-01 | Gas release / Explosion / Toxic | Battery cell | Any (often discovered during response) | Cell venting into poorly ventilated enclosure | Cell off-gassing without ignition (e.g. internal short) in a closed enclosure | Flammable gas accumulates above LFL because exhaust ventilation is off/failed or not triggered | Vent gas (H2, CO, hydrocarbons) accumulates ignition source (arc, hot cell, door opened admitting air) deflagration | Explosive atmosphere deflagration enclosure rupture follow-on fire | Firefighter/technician opening the door or standing in front of the enclosure is hit by deflagration overpressure, fireball and flying door/panels (cf. McMicken 2019). | Firefighters, O&M technicians | Explosion | Explosion Fire Toxic | Gas concentration (H2 / CO / VOC) % LFL | SF-12 | OK
GX-02 | Gas release / Explosion / Toxic | Battery cell | Inspection / maintenance | Electrolyte leak from damaged cell | Cell casing breach (swollen/damaged cell, seal failure) | Liquid electrolyte leaks; reacts with moisture forming HF; flammable vapour | Leak flammable/corrosive vapour in module exposure on opening module; possible ignition | Flammable vapour HF formation chemical contamination possible fire | Technician opening the module inhales HF / electrolyte vapour or gets skin/eye contact → chemical burns, poisoning. | O&M technicians | Toxic | Toxic Chemical burn Fire | Electrolyte vapour / VOC detection; visual swelling | SF-11 | OK
GX-03 | Gas release / Explosion / Toxic | Thermal management (HVAC) | Any | HVAC refrigerant leak into occupied enclosure | Refrigerant leak inside enclosure (A1 high concentration, or flammable A2L/A3 refrigerant) | Refrigerant displaces oxygen or forms flammable mixture | Leak O2 depletion or flammable atmosphere asphyxiation / ignition | Oxygen-deficient atmosphere flammable mixture fire | Technician entering walk-in enclosure is asphyxiated or exposed to flash fire. | O&M technicians | Asphyxiation | Asphyxiation Fire | Refrigerant / O2 detector | SF-29 | OK
SH-01 | Electric shock / Arc flash (DC) | DC electrical | Normal operation / maintenance | Undetected first DC ground fault | DC insulation fault to earth (cable abrasion, moisture) not detected (IMD failed or alarm ignored) | First fault makes one pole earth-referenced; second fault → short circuit | Pole at earth potential touching other pole = full DC voltage; second fault high-current short arc/fire | Hidden touch-voltage hazard double ground fault short arc fire | Technician touching a 'safe' DC conductor while standing on earth receives up to 1500 VDC shock. Personnel exposed to arc/fire from second fault. | O&M technicians | Electric shock | Electric shock Arc flash Fire | Insulation resistance (IMD) value | SF-17 | OK
SH-02 | Electric shock / Arc flash (DC) | People & lifecycle | Maintenance | Maintenance on rack that cannot be fully de-energized | Stranded energy: series-connected modules are always energized even with contactors open | Work on 'isolated' rack, contact across module links or tool drop across terminals | Contact with live inter-module busbar shock; tool bridging short arc | Electric shock DC arc flash module damage | Technician working on the rack contacts live inter-module conductors → electric shock / arc flash burns. | O&M technicians | Electric shock | Electric shock Arc flash | — |  | none
SH-03 | Electric shock / Arc flash (DC) | PCS | Maintenance | Residual energy in PCS DC-link after isolation | DC-link capacitor discharge resistor failed | Capacitors remain charged after isolation | Technician opens PCS assuming de-energized contacts charged capacitor | Stored-energy discharge shock arc | Technician touches charged DC-link bus → electric shock / burns. | O&M technicians | Electric shock | Electric shock Arc flash | DC-link voltage indication | SF-19 | OK
SH-04 | Electric shock / Arc flash (DC) | People & lifecycle | Maintenance / measurement | Short circuit during live DC work | Live work on DC equipment (measurement, fuse replacement) | Probe slip / tool drop / wrong test equipment causes short | Arc initiation DC arc does not self-extinguish arc flash | DC arc flash molten metal blast | Technician performing the work is exposed to arc flash → burns, eye injury. | O&M technicians | Arc flash | Arc flash | — |  | none
SH-05 | Electric shock / Arc flash (DC) | External / site | Any | Loss of protective earth connection | Loss of protective earth (corrosion, loose joint, copper theft) combined with insulation fault | Enclosure / fence becomes energized | Insulation fault energizes exposed conductive part with no fault path no protection trip | Energized enclosure / fence touch voltage | Worker or member of public touching the enclosure/fence receives electric shock. | O&M technicians, public | Electric shock | Electric shock | Earth continuity monitoring; touch-voltage measurement | SF-18 | OK
SH-06 | Electric shock / Arc flash (DC) | External / site | Any | Unauthorized entry into energized BESS area | Unauthorized access (intruder, copper theft, vandalism) | Contact with live parts or damage to equipment | Contact with live conductors; cable cutting short arc/fire | Electric shock arc fire | Intruder contacts live parts → electrocution / burns; later fire endangers responders. | Public / intruders, firefighters | Electric shock | Electric shock Arc flash Fire | Door switch / intrusion alarm | SF-33 | OK
GR-01 | Grid interface / AC side | PCS | Grid outage | Anti-islanding failure during grid outage | Grid outage / upstream breaker opens | PCS fails to detect island (detection failure, wrong settings) and continues to energize the disconnected section | BESS keeps islanded feeder energized line assumed dead | Unintentional island energized 'dead' line out-of-phase reclosing risk | Utility line worker contacts line believed de-energized → electrocution. | Utility line workers | Electric shock | Electric shock | Loss of grid (V/f/ROCOF/vector shift) | SF-20 | OK
GR-02 | Grid interface / AC side | PCS | Maintenance on AC side | Unintended PCS restart back-feeds equipment under maintenance | PCS automatic restart logic re-enables output on grid return or after alarm reset | PCS starts while downstream transformer / MV cable is under maintenance and back-feeds it | PCS energizes transformer / MV cable worker contact | Energized equipment under work arc | Worker on transformer/MV cable is electrocuted or exposed to arc flash. | O&M technicians, contractors | Electric shock | Electric shock Arc flash | Breaker/isolator position; LOTO status | SF-22 | OK
GR-03 | Grid interface / AC side | Grid / AC equipment | Operation / switching | Internal arc fault in MV switchgear | Internal insulation failure (partial discharge, contamination, rodent) or maloperation (closing onto earth) | Internal arc in switchgear | Arc pressure rise, hot gas release, panel rupture | Internal arc pressure wave hot gas switchgear fire | Operator standing in front of switchgear during switching is exposed to arc blast and hot gases → burns, blast injury. | Operators | Arc flash | Arc flash Fire | Partial discharge; arc detection (light + current) | SF-23 | OK
GR-04 | Grid interface / AC side | Grid / AC equipment | Normal operation | Transformer internal fault | Winding insulation failure (overload, harmonics from PCS, DC injection saturation, aging) | Internal arc in oil → gas generation → tank pressure | Arc in oil tank rupture oil spill fire fire exposure to BESS | Transformer explosion oil pool fire fire spread to BESS (→ EX-01) | Personnel near transformer exposed to blast, burning oil and radiant heat. | O&M technicians, firefighters | Fire | Fire Explosion | Buchholz / sudden pressure; winding & oil temperature; DGA | SF-24 | OK
GR-05 | Grid interface / AC side | Grid / AC equipment | Grid fault | AC fault not cleared by protection | Short circuit on AC side with protection miscoordination or breaker failure to trip | Sustained fault current through PCS output cables | Sustained overcurrent cable/busbar overheating fire; arc | Cable fire arc PCS damage | Personnel near PCS/cable route exposed to fire and toxic smoke. | O&M technicians, firefighters | Fire | Fire Arc flash Toxic | Fault current; breaker status | SF-25 | OK
GR-06 | Grid interface / AC side | Grid / AC equipment | Reconnection / auto-reclose | Out-of-phase connection to grid | Synchronization / sync-check failure or utility auto-reclose onto energized island | Out-of-phase closure → very high transient current | Transient overcurrent IGBT / capacitor rupture PCS explosion / fire | PCS component rupture projectiles PCS fire | Person near PCS cabinet exposed to projectiles, blast and fire. | O&M technicians | Explosion | Explosion Fire | Phase angle / voltage difference at breaker | SF-20, SF-21 | OK
GR-07 | Grid interface / AC side | PCS | Normal operation | PCS power-semiconductor failure | IGBT failure (short) with desaturation protection failure | Shoot-through discharges DC-link capacitors / battery into power stage | Shoot-through capacitor/IGBT rupture arc PCS cabinet fire | PCS explosion arc cabinet fire | Technician near PCS exposed to blast, arc and fire. | O&M technicians | Fire | Fire Explosion Arc flash | Desat signal; DC-link current | SF-06 | OK
GR-08 | Grid interface / AC side | PCS | Normal operation | AC filter capacitor overstress | Grid overvoltage or harmonic resonance | Filter capacitors overheat | Capacitor overheating rupture fire | Capacitor rupture PCS fire | Personnel near PCS exposed to fire/smoke. | O&M technicians | Fire | Fire | Harmonic distortion; capacitor temperature/current | SF-26 | OK
CS-01 | Control / Software / Cyber | BMS | Commissioning / after update | Incorrect BMS protection settings (systematic fault) | Wrong BMS protection parameters (firmware update error, wrong cell-chemistry profile, commissioning error) | BMS OV / OT / OC limits set beyond cell safe limits → BMS never requests stop or opens contactor | Operation beyond safe window with no trip overcharge / overtemperature TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Parameter checksum / configuration audit | SF-01, SF-10, SF-34 | OK
CS-02 | Control / Software / Cyber | EMS / SCADA | Any | Cyber attack on BESS control systems | Cyber intrusion into EMS/SCADA/BMS | Malicious setpoints, disabled alarms/protections, falsified BMS data, HVAC shut off | Forced overcharge / overcurrent / cooling loss while protections suppressed TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Unauthorized config change; abnormal commands | SF-01, SF-10 | OK
CS-03 | Control / Software / Cyber | BMS | Normal operation | BMS processor freeze with frozen data | BMS processor hang / software freeze (watchdog failed) | Last values kept being reported as 'normal'; control and protection functions in BMS stop | PCS keeps operating on stale 'healthy' data overcharge / overtemperature undetected TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Heartbeat / data freshness counter | SF-02, SF-03 | OK
CS-04 | Control / Software / Cyber | PCS | Commissioning / after update | Incorrect PCS limit settings (systematic fault) | Wrong PCS limit parameters (max DC charge voltage/current set too high, wrong battery profile loaded in PCS) | PCS own limits no longer backstop the BMS; any BMS or EMS command error is passed straight to the battery | Charge beyond battery rating is accepted by PCS overcharge / overcurrent TR | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | PCS parameter vs approved baseline; DC V/I above battery rating | SF-01, SF-06, SF-34 | OK
AU-01 | Auxiliary / Suppression systems | Auxiliary & safety systems | Grid outage / aux fault | Loss of auxiliary power to safety-supporting systems | Loss of auxiliary power (aux transformer fault, grid loss with failed UPS) | BMS, HVAC, gas detection, ventilation and fire detection lose power | No cooling/monitoring developing TR (any cause) undetected; gas accumulates; long outage may deep-discharge cells ( OD-01) | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS loss of detection and mitigation | Technician/firefighter at or near the container is exposed to fire, jet flame and radiant heat → burns. Person opening or standing at the enclosure door is exposed to deflagration overpressure, fireball and projectiles (door, panels). Personnel/public downwind inhale toxic combustion gases (HF, CO, HCN) → poisoning. | O&M technicians, firefighters, public near site fence / downwind | Fire | Fire Explosion Toxic | Aux voltage; UPS status | SF-04, SF-12, SF-27 | OK
AU-02 | Auxiliary / Suppression systems | Auxiliary & safety systems | Maintenance (person inside) | Inadvertent suppression discharge with personnel inside | Spurious or manual release of suppression agent (detector false trip, wrong release, no lock-off) | Agent discharge into occupied walk-in enclosure | O2 depletion / agent toxicity / decomposition products; discharge noise and pressure | Oxygen-deficient / toxic atmosphere | Technician inside the enclosure is asphyxiated or poisoned. | O&M technicians | Asphyxiation | Asphyxiation Toxic | Door status; occupancy; release circuit status | SF-28 | OK
AU-03 | Auxiliary / Suppression systems | Auxiliary & safety systems | Normal operation | Hydrogen generation from UPS batteries | UPS charger overvoltage / battery thermal runaway (lead-acid) | Excess H2 evolution in room with failed ventilation | H2 accumulates ignition explosion | H2 explosion fire in control room | Person in control/aux room exposed to explosion and fire. | Operators, O&M technicians | Explosion | Explosion Fire | H2 concentration; float voltage | SF-12, SF-30 | OK
LC-01 | Lifecycle (transport → decommissioning) | People & lifecycle | Transport / storage | Transport/storage damage to modules | Module abused in transport/storage (drop, vibration, heat exposure) | Latent internal damage | Hidden damage internal short TR in warehouse, on truck, or after installation | Cell thermal runaway (TR) → propagation to adjacent cells/modules flammable + toxic vent gas (H2, CO, HF, VOC) release module/rack fire possible deflagration in enclosure fire spread to adjacent containers/PCS | Warehouse/transport/installation personnel exposed to fire, explosion, toxic gas. | Logistics workers, installers | Fire | Fire Explosion Toxic | Shock logger; incoming inspection (OCV, IR) |  | none
LC-02 | Lifecycle (transport → decommissioning) | People & lifecycle | Commissioning | Wiring error at first energization | Wiring error (reverse polarity, wrong series/parallel connection) | Short circuit or reverse current at first energization | Short/reverse current arc fire / equipment damage | Arc flash fire component damage | Commissioning engineer exposed to arc flash / fire. | Commissioning engineers | Arc flash | Arc flash Fire | Polarity / voltage check before closing | SF-32 | OK
LC-03 | Lifecycle (transport → decommissioning) | People & lifecycle | Maintenance (module/rack replacement) | Voltage mismatch on paralleling strings | New module/rack at different SOC/voltage connected in parallel | High circulating current between strings | Circulating current overcurrent arc at contactor / cell overheating | Arc contactor damage cell overheating / TR | Technician connecting the string exposed to arc flash; later fire. | O&M technicians | Arc flash | Arc flash Fire | String voltage difference before closing | SF-31 | OK
LC-04 | Lifecycle (transport → decommissioning) | People & lifecycle | Decommissioning / recycling | Short circuit during decommissioning | Handling modules with unknown SOC or damage | Short circuit during dismantling / cutting | Short arc TR of retired module | Arc fire TR toxic gas | Dismantling worker exposed to arc, fire and toxic gas. | Decommissioning workers | Fire | Fire Arc flash Toxic | SOC / voltage before dismantling |  | none
ER-01 | Emergency response / Post-fire | People & lifecycle | Post-incident | Re-ignition of fire-damaged battery | Stranded energy in damaged cells after fire is extinguished | Damaged cells re-enter TR hours/days later | Re-ignition during overhaul / removal fire, gas release | Re-ignition fire toxic gas shock from damaged live parts | Firefighters/recovery crew handling debris exposed to re-ignition fire, toxic gas and electric shock. | Firefighters, recovery crew | Fire | Fire Toxic Electric shock | Thermal imaging; gas monitoring |  | none
ER-02 | Emergency response / Post-fire | People & lifecycle | Firefighting | Firefighting water on energized BESS | Water application on equipment that is still energized | Conduction through hose stream / pooled water | Current path through water to firefighter; possible electrolysis/H2 | Electric shock H2 generation | Firefighter applying water is electrocuted. | Firefighters | Electric shock | Electric shock Explosion | Isolation status indication for responders | SF-33 | OK

## Safety functions
SF ID | Safety function | Type | Sensor (S) | Measured variable | Logic solver (L) | Final element (A) | Final element tags (; separated) | Safe state | Demand mode | Must not share (independence) | Reference | Check: scenarios citing this SF
SF-01 | Cell overvoltage trip | SIF candidate | Independent cell-voltage monitor (secondary AFE / hardware OV comparator per cell) | Cell voltage (each cell) | Independent protection board or safety PLC / safety relay (not the main BMS CPU) | Rack DC contactor (de-energize to open) + PCS DC breaker shunt trip | DC contactor; DC breaker | Charging stopped, battery isolated from PCS | Low demand → PFDavg | Must NOT share voltage sensor, CPU, software or power with BMS charge control (see independence section of attachment). Hard-coded threshold, not configurable via EMS. | IEC 61508 / 61511, IEC 62619, IEC 62933-5-2 | 9
SF-02 | Communication-loss / watchdog → PCS to zero power | Control-level protection (usually not credited as IPL) | Heartbeat / data-freshness counter on BMS–PCS link | Message age, counter increment | PCS controller watchdog function | PCS gate-blocking (power stage off) / PCS AC contactor | PCS power stage / AC contactor | PCS output = 0 kW | Low demand | Resides in the same PCS controller that may cause OV-01 → cannot be IPL for OV-01; OK as IPL for OV-02 only if PCS is independent of the failed link. | IEC 62933-5-2 | 2
SF-03 | External BMS watchdog → safe state | SIF candidate / fail-safe design | Watchdog pulse from BMS processor | Pulse present / missing | External hardware watchdog IC / timer relay | Rack DC contactor coil drop-out | DC contactor | Contactors open | Low demand | Watchdog must be external to the monitored processor and have its own power. | IEC 61508-2/-3 | 1
SF-04 | Cell undervoltage trip + charge-inhibit lockout | SIF candidate | Cell-voltage monitor | Cell voltage (min) | BMS or independent protection board | Rack DC contactor + latched 'charge inhibit' flag to PCS | DC contactor; Start/close/charge inhibit | Discharge stopped; recharge blocked until inspection | Low demand | Lockout must survive power cycling (non-volatile). Independent of SOC algorithm. | IEC 62619 | 2
SF-05 | Low-temperature charge inhibit | SIF candidate | Cell temperature sensors (NTC) | Cell temperature | BMS / protection board | PCS charge-current limit = 0 and/or DC contactor | PCS power stage / AC contactor; DC contactor | No charging below T_min | Low demand | Should not rely on the same NTC used for heater control. | IEC 62619 | 1
SF-06 | Overcurrent trip (DC) | SIF candidate / self-acting protection | Rack current sensor (shunt / Hall) independent of PCS current sensor – or fuse element (sensor+logic+actuator in one) | DC current | Independent protection board / DC breaker trip unit (fuse = no logic solver) | DC breaker / rack fuse / contactor | DC breaker; Fuse; DC contactor | Current interrupted | Low demand (check – if trips often, fix design) | Do not use PCS current sensor (shared with IE OC-01). Contactors must be rated to break fault current, otherwise fuse/breaker must do it. | IEC 60947-2, IEC 60269 | 4
SF-07 | DC arc-fault detection and interruption | SIF candidate | Arc-fault detector (HF current signature) | Arc signature on DC conductors | AFD relay | DC breaker shunt trip | DC breaker | Arc extinguished, circuit open | Low demand | Nuisance-trip vs detection trade-off; test regularly. | UL 1699B (PV analogue), IEC 63027 | 2
SF-08 | Contactor weld detection | Diagnostic + trip | Contactor auxiliary contact + voltage across main contacts | Commanded vs actual contact state | BMS / protection board | Upstream DC breaker shunt trip + 'not isolated' indication | DC breaker; Indication / alarm | Circuit isolated by second device; HMI shows 'still energized' | Low demand | Upstream breaker must be a different device type (diversity) from the welded contactor. | IEC 60947-4-1 | 1
SF-09 | Hot-joint / connection monitoring | Detection → derate/trip | Busbar/terminal temperature sensors or ΔV across joints | Joint temperature / voltage drop | BMS | PCS derate command → DC contactor if high-high | PCS power stage / AC contactor; DC contactor | Reduced current or isolation | Low demand | Derate part is normal control; only high-high trip is a safety function. | — | 1
SF-10 | Cell overtemperature trip | SIF candidate | Redundant / diverse cell temperature sensors (NTC + independent thermal sensor) | Cell / module temperature | Independent protection board or safety PLC | PCS stop + rack DC contactor open | PCS power stage / AC contactor; DC contactor | No current; heat generation stopped | Low demand → PFDavg | Sensor independent from HVAC control sensor and from BMS derating loop. | IEC 62619, IEC 62933-5-2 | 5
SF-11 | Off-gas detection → isolate | SIF candidate (early warning) | H2 / CO / VOC (electrolyte vapour) detectors in module or enclosure | Gas concentration | Gas-detection controller or safety PLC | Rack DC contactors + PCS trip + alarm | DC contactor; PCS power stage / AC contactor; Indication / alarm | Battery isolated before TR develops | Low demand | Detects TR regardless of cause → good diverse layer. Controller on UPS. | UL 9540A, NFPA 855 | 10
SF-12 | Explosion-prevention exhaust ventilation | SIF candidate (mitigation) | Flammable gas detectors (H2 / %LFL) | Gas concentration (%LFL) | Gas panel / safety PLC (UPS-backed) | Exhaust fan(s) + inlet louvres/dampers open | Ventilation fan / damper | Gas kept below 25 % LFL | Low demand | Fans, detectors and controller must stay powered when main aux fails (AU-01). Fan failure alarm. | NFPA 69, NFPA 855 | 4
SF-13 | Coolant leak detection → stop & isolate | SIF candidate | Leak-detection cable / coolant pressure or level switch | Liquid presence / pressure drop | TMS controller or BMS | Coolant pump stop + rack DC contactor | Pump; DC contactor | No flow onto live parts; battery isolated | Low demand | Pump stop removes cooling → combine with SF-10 logic. | — | 1
SF-14 | Seismic / impact trip | SIF candidate | Seismic switch / accelerometer / impact sensor | Ground acceleration / shock | Safety relay | All DC contactors + PCS AC breaker | DC contactor; AC breaker | Site de-energized | Low demand | Final elements shared with SF-01/SF-10 → common-cause watch. | — | 2
SF-15 | Flood detection trip | SIF candidate | Water level switch in enclosure base / cable trench | Water level | Safety relay | DC contactors + PCS AC breaker + interface breaker | DC contactor; AC breaker; Interface (POI) breaker | Site de-energized before water reaches live parts | Low demand | Sensor below lowest live part; relay mounted above flood level. | — | 1
SF-16 | Fire detection → isolation (and suppression) | SIF candidate / fire system | Smoke / heat / flame detectors | Smoke, temperature, flame | Fire alarm control panel (FACP) | DC contactors + PCS trip + suppression release + alarm | DC contactor; PCS power stage / AC contactor; Suppression release; Indication / alarm | Battery isolated, fire controlled | Low demand | FACP is separate standard (EN 54 / NFPA 72); interface to BMS trip must be hardwired. | NFPA 72, NFPA 855, EN 54 | 4
SF-17 | Insulation monitoring (IMD) | Detection → alarm/trip | Insulation monitoring device | Insulation resistance DC+/DC– to earth | IMD relay (built-in logic) | Alarm → PCS DC breaker trip on low-low | DC breaker; Indication / alarm | No hidden earth fault | Low demand | One IMD per galvanically connected DC system; parallel IMDs interfere. | IEC 61557-8 | 5
SF-18 | Earth continuity / touch-voltage monitoring | Detection → alarm/trip | Earth continuity monitor / RCM | PE loop resistance / residual current | Monitoring relay | Alarm / supply breaker trip | AC breaker; Indication / alarm | Exposed parts not energized | Low demand | — | IEC 61557-8/-11 | 1
SF-19 | Voltage-present door interlock | Interlock | DC-link / bus voltage detector | Residual voltage | Interlock relay | Door lock solenoid (locked while V > safe limit) | Door lock | Door cannot be opened while energized | Low demand | Fail-safe: loss of power = door locked (with emergency override). | ISO 14119 (concept) | 2
SF-20 | Anti-islanding / loss-of-mains trip | SIF candidate / protection relay | VTs / CTs at point of interconnection | Voltage, frequency, ROCOF, vector shift | Independent interface protection relay (not PCS internal) | Interface / POI circuit breaker (+ PCS stop) | Interface (POI) breaker; PCS power stage / AC contactor | BESS disconnected from de-energized grid | Low demand | PCS internal anti-islanding shares PCS controller → only one layer. External relay = independent layer. | IEEE 1547, IEC 62116, local grid code | 2
SF-21 | Synchronism-check interlock (ANSI 25) | Interlock / protection | VTs on both sides of breaker | ΔV, Δf, Δphase | Sync-check relay | Breaker close-permissive (block closing) | Start/close/charge inhibit | Breaker stays open if out of phase | Low demand | — | IEEE C37.2 (25) | 1
SF-22 | Maintenance start-inhibit interlock | Interlock | Isolator / earth-switch position contacts, trapped-key / LOTO switch | Isolation status | Hardwired interlock relay | PCS enable signal removed + breaker close blocked | Start/close/charge inhibit | PCS cannot start / back-feed | Low demand | Hardwired, not via EMS software (auto-restart logic is the IE). | — | 1
SF-23 | MV switchgear arc-flash protection | Protection relay | Light (arc) sensors + CT overcurrent | Arc light + overcurrent | Arc-flash relay | Upstream breaker trip | AC breaker | Arc cleared in < ~100 ms | Low demand | Light AND current (2-criteria) to avoid spurious trips. | IEC 62271-200 (IAC) | 1
SF-24 | Transformer protection (63 / 87T / 26 / 49) | Protection relay | Buchholz relay, sudden-pressure relay, differential CTs, oil / winding temp | Gas, pressure, differential current, temperature | Transformer protection relay | HV and LV breakers | AC breaker | Transformer de-energized | Low demand | — | IEC 60076, IEEE C37.91 | 1
SF-25 | Breaker-failure protection (50BF) | Protection relay | CTs | Current after trip command | Protection relay | Upstream (backup) breaker | AC breaker | Fault cleared by backup | Low demand | Backup breaker must be separate from failed breaker. | IEEE C37.119 | 1
SF-26 | AC filter capacitor protection | Protection | CT / capacitor temperature sensor | Filter current, harmonics, temperature | PCS protection function | Filter contactor / PCS trip | PCS power stage / AC contactor | Filter disconnected | Low demand | Inside PCS controller → limited independence. | — | 1
SF-27 | Loss-of-auxiliary-power fail-safe | Fail-safe design | Aux voltage relay / UPS status (or inherent: contactor coil powered by aux) | Aux supply present | Hardwired (de-energize-to-trip) | Rack DC contactors open; safety systems stay on UPS | DC contactor | Battery isolated when monitoring is lost | Low demand | De-energize-to-trip makes this inherently safe; verify UPS autonomy for detection/ventilation. | IEC 61508 (fail-safe principle) | 1
SF-28 | Suppression lock-off / occupancy interlock | Interlock | Door switch, occupancy sensor, lock-off valve / key position | Personnel present | Suppression release panel | Release inhibit + pre-discharge alarm/strobe + time delay | Start/close/charge inhibit; Indication / alarm | No discharge while occupied | Low demand | Must not disable automatic protection when unoccupied (auto-restore). | ISO 14520, NFPA 2001 | 1
SF-29 | Refrigerant / O2 detection → ventilate | Detection → action | Refrigerant or O2 sensor | Refrigerant ppm / O2 % | Gas controller | Ventilation fan + entry warning beacon | Ventilation fan / damper; Indication / alarm | Safe atmosphere before entry | Low demand | — | ISO 5149, EN 378 | 1
SF-30 | UPS charger overvoltage protection | Protection | Battery-voltage sensing | Float / charge voltage | Charger protection circuit | Charger output off | Charger output | No overcharge of VRLA → no excess H2 | Low demand | — | IEC 62485-2 | 1
SF-31 | Voltage-match interlock for paralleling strings | Interlock | String voltage measurement | ΔV between string and DC bus | BMS master | Block contactor close | Start/close/charge inhibit | No closing onto large ΔV | Low demand | — | — | 1
SF-32 | Polarity-check interlock | Interlock | Voltage polarity measurement | Polarity / expected voltage | BMS / commissioning tool | Block contactor close | Start/close/charge inhibit | No energization of mis-wired string | Low demand | — | — | 1
SF-33 | Emergency stop / remote isolation (ESD) with status indication | Manual SIF / E-stop | E-stop pushbuttons (local + remote/fire-panel) | Operator action | Hardwired ESD loop / safety relay | All DC contactors + PCS AC breaker + interface breaker; 'isolated' indicator for responders | DC contactor; AC breaker; Interface (POI) breaker; Indication / alarm | Whole BESS isolated | Low demand | Human is the 'sensor' → LOPA credit limited. Note: DC modules remain internally live (stranded energy). | ISO 13850 (concept), NFPA 855 | 2
SF-34 | Parameter integrity check at start-up | Software diagnostic | Configuration checksum / signed firmware | Parameter set vs approved baseline | BMS / PCS bootloader | Start inhibit | Start/close/charge inhibit | System does not run with unapproved limits | On-demand at start | Systematic-fault measure; complements (does not replace) hard-coded SF-01/SF-10. | IEC 61508-3, IEC 62443 | 2

## Other measures
Measure | Scenarios (comma-separated)
Passive – propagation barriers / cell spacing | IC-01, all TR
Passive – bollards / crash barriers | ME-01
Passive – separation distance / fire-rated walls | EX-01, GR-04
Passive – deflagration vents / explosion panels | GX-01
Passive – lightning protection system + SPD | EX-03
Passive – ingress protection (IP rating, sealing) | EX-04, EX-05
Passive – IAC-rated switchgear, pressure relief | GR-03
Design – module service disconnect / plug | SH-02
Design – hardwired (non-networked) safety trips; network zoning | CS-02
Admin – de-energized work policy, LOTO, PPE | SH-02, SH-04, GR-02
Admin – lifting plan | ME-03
Admin – incoming inspection and quarantine | LC-01, ME-03
Admin – SOH-based retirement | IC-02
Admin – discharge-to-safe-SOC before dismantling | LC-04
Admin – post-fire monitoring & emergency response plan | ER-01, ER-02
Admin – site security / fencing | SH-06
Admin – management of change for parameters/firmware | CS-01

## Lists
Component | Colour (hex) | PCS/BMS panel text (leave empty = not in panel) | Group (display order) | Hazard type | Icon | Show as filter (Y/N) | SF type filter chips (keyword in 'Type')
PCS | #5aa9ff | Power conversion: follows setpoints, converts DC↔AC. | Overcharge / Overvoltage | Fire | 🔥 | Y | SIF candidate
BMS | #a78bfa | Battery management: measures cells, computes limits, commands stop. | Overdischarge / Low-temperature charging | Explosion | 💥 | Y | Protection
BMS–PCS comm link | #2dd4bf | The link that carries BMS limits to the PCS. | Overcurrent / Short circuit | Toxic | ☠️ | Y | Interlock
Battery cell | #fbbf24 |  | Internal cell defect | Electric shock | ⚡ | Y | Detection
DC electrical | #fb923c |  | Thermal management / Overtemperature | Arc flash | ✴️ | Y | Fail-safe
Thermal management (HVAC) | #67e8f9 |  | Mechanical / External damage | Asphyxiation | 🫁 | Y | Manual
Grid / AC equipment | #60a5fa |  | External fire / Environment | Mechanical | ⚙️ | Y | Diagnostic
EMS / SCADA | #f472b6 |  | Gas release / Explosion / Toxic | Chemical burn | 🧪 | N | Control-level
Auxiliary & safety systems | #4ade80 |  | Electric shock / Arc flash (DC)
External / site | #a3a3a3 |  | Grid interface / AC side
People & lifecycle | #fda4af |  | Control / Software / Cyber
Auxiliary / Suppression systems
Lifecycle (transport → decommissioning)
Emergency response / Post-fire

## Page text
Key (do not change) | Text
title | Hazardous scenarios in a grid-connected BESS
subtitle | Each scenario is written as in step 1 of the LOPA: one initiating event, the sequence it starts, what physically happens, and how a person gets hurt. Every initiating event belongs to one component only, so PCS and BMS failures are separate scenarios.
owners_heading | PCS, BMS and the link between them
owners_intro | Your example says "PCS / BMS charging control fails". These are different failures with different independence problems, so they are split. If the PCS is the cause, a BMS-based trip can be credited; if the BMS is the cause, only a trip that does not use the BMS sensor, CPU or software can be credited.
reuse_warning | The rack DC contactor carries most of the load. A welded contactor (scenario [OC-03]) defeats every function that relies on it. A diverse second final element, such as a DC breaker with shunt trip, gives a 1oo2 path to the safe state.
home_url | Main_IEC61508_Safety_Lifecycle_Overview.html
home_label | Home · IEC 61508 Safety Lifecycle
home_url: file name of the home page. Same folder = just the file name; other folder = relative path with / and ../ (e.g. ../Main_IEC61508_Safety_Lifecycle_Overview.html).

## Checks
Check | Value
Scenarios | 56
Safety functions | 34
Scenarios with no SF (passive/admin only) | 7
Scenarios with unknown SF ID | 0
Safety functions not cited by any scenario | 0
Scenarios with component not in Lists | 0
Scenarios with group not in Lists | 0
Expected: last four checks = 0 before rebuilding the HTML.